## Sheet1
| index | Point_Description | Point_Name | ALARM DELAY | NOTIFICATION LEVEL
0 | 0 |  | DAHU
1 | 1 | Evaporative Cooler 1 Stage 1 Flow Alarm | [EVAP1][STG1][FLOW][ALM] | 5 sec | High
2 | 2 | Evaporative Cooler 1 Stage 2 Flow Alarm | [EVAP1][STG2][FLOW][ALM] | 5 sec | High
3 | 3 | Evaporative Cooler 2 Stage 1 Flow Alarm | [EVAP2][STG1][FLOW][ALM] | 5 sec | High
4 | 4 | Evaporative Cooler 2 Stage 2 Flow Alarm | [EVAP2][STG2][FLOW][ALM] | 5 sec | High
5 | 5 | UPS Power Status | [PWR][UPS][STATUS] | 5 sec | High
6 | 6 | Mode Alarm | [BMS][MODE][ALM] | 5 sec | High
7 | 7 | Supply Air Temp Setpoint Alarm | [BMS][SAT][STPT][ALM] | 5 sec | High
8 | 8 | Supply Fan Speed Alarm | [BMS][SF][SPD][ALM] | 5 sec | Medium
9 | 9 | Bypass Damper Lower Limit Alarm | [BYPD][LOWER][ALM] | 60 sec | Medium
10 | 10 | Bypass Damper Upper Limit Alarm | [BYPD][UPPER][ALM] | 60 sec | High
11 | 11 | Evap Cooler Fan Failure Alarm | [ECFAN][FAIL][ALM] | 5 sec | High
12 | 12 | Command | [FEC][CMD] | 30 secs | Medium
13 | 13 | Evaporative Cooler P High Water Alarm | [EVAP][HIGH][WATER][ALM] | 5 sec | High
14 | 14 | Evaporative Cooler P Low Water Alarm | [EVAP][LOW][WATER][ALM] | 5 sec | High
15 | 15 | Lower Limit Status | [FEC][LOWER][STS] | 60 sec | Medium
16 | 16 | Upper Limit Status | [FEC][UPPER][STS] | 2 minute | Medium
17 | 17 | Filter Differential Pressure Alarm | [FILDP][ALM] | 5 sec | Medium
18 | 18 | Pre-Filter | [PREFILTER] | 5 sec | Medium
19 | 19 | Final Filter | [FINALFILTER] | 5 sec | Medium
20 | 20 | Supply Air Damper Lower Limit Alarm | [SAD][LOWER][ALM] | 5 sec | Medium
21 | 21 | Supply Air Damper Upper Limit Alarm | [SAD][UPPER][ALM] | 30 sec | Medium
22 | 22 | Supply Air Temp High Alarm | [SAT][HIGH][ALM] | 30 sec | Medium
23 | 23 | Supply Air Temp Low Alarm | [SAT][LOW][ALM] | 5 sec | Medium
24 | 24 | Level Alarm | [SUMP1][HI][LVL][ALM] | 5 sec | High
25 | 25 | Low Level Alarm | [SUMP1][LOW][LVL][ALM] | 5 sec | High
26 | 26 | Pump Alarm | [SUMP1][PMP][ALM] | 5 sec | High
27 | 27 | Level Alarm | [SUMP2][HI][LVL][ALM] | 5 sec | High
28 | 28 | Low Level Alarm | [SUMP2][LOW][LVL][ALM] | 5 sec | High
29 | 29 | Pump Alarm | [SUMP2][PMP][ALM] | 5 sec | High
30 | 30 | UPS Power | [UPS][POWER] | 5 sec | High
31 | 31 | UPS Power | [UPS][POWER] | 5 sec | High
32 | 32 | Supply Air Temp Temperature Sensor 1 | [SAT][T1] | 5 sec | High
33 | 33 | Supply Air Temp Temperature Sensor 2 | [SAT][T2] | 5 sec | High
34 | 34 | Supply Air Temp | [SAT] | 30 sec | High
35 | 35 | Dedicated AHU Supply Fan Alarm | [DAHU][SF][ALM] | 5 sec | High
36 | 36 | Dedicated AHU Filter Differential Pressure Alarm | [DAHU][FILDP][ALM] | 5 sec | Medium
37 | 37 | Dedicated AHU Supply Air Temp High Alarm | [DAHU][SAT][HIGH][ALM] | 30 sec | Medium
38 | 38 | Air Handling Unit Supply Fan Alarm | [AHU][SF][ALM] | 5 sec | High
39 | 39 | Air Handling Unit Filter Differential Pressure Alarm | [AHU][FILDP][ALM] | 5 sec | Medium
40 | 40 | Air Handling Unit Supply Air Temp Low Alarm | [AHU][SAT][LOW][ALM] | 5 sec | Medium
41 | 41
42 | 42
43 | 43 |  | INDUSTRIAL WATER SYSTEM
44 | 44 | Industrial Water Pump Failure Alarm | [IWS][PUMP][FAIL][ALM] | 5 sec | High
45 | 45 | Industrial Water Tank High Level Alarm | [IWS][TANK][HIGH][LVL][ALM] | 5 sec | High
46 | 46 | Industrial Water Tank Low Level Alarm | [IWS][TANK][LOW][LVL][ALM] | 5 sec | High
47 | 47 | Industrial Water Flow Alarm | [IWS][FLOW][ALM] | 5 sec | Medium
48 | 48 | Industrial Water Filter Differential Pressure Alarm | [IWS][FILDP][ALM] | 5 sec | Medium
49 | 49 | Industrial Water Supply Pressure Low Alarm | [IWS][SUPPLY][PRESSURE][LOW][ALM] | 5 sec | High
50 | 50
51 | 51 |  | ELECTRICAL ROOM
52 | 52 | Main Breaker Trip Alarm | [ELEC][MAIN][BRKR][TRIP][ALM] | 5 sec | High
53 | 53 | Panel Overheat Alarm | [ELEC][PNL][OVERHEAT][ALM] | 10 sec | High
54 | 54 | UPS Failure Alarm | [ELEC][UPS][FAIL][ALM] | 5 sec | High
55 | 55 | Room Temperature High Alarm | [ELEC][ROOM][TEMP][HIGH][ALM] | 30 sec | Medium
56 | 56 | Smoke Detection Alarm | [ELEC][SMOKE][ALM] | 5 sec | High
57 | 57 | Power Loss Alarm | [ELEC][POWER][LOSS][ALM] | 5 sec | High
58 | 58 | Generator Running Status | [ELEC][GEN][RUN][STS] | 5 sec | Medium
59 | 59 | Battery Low Alarm | [ELEC][BATTERY][LOW][ALM] | 10 sec | High
60 | 60 | Surge Protection Device Alarm | [ELEC][SPD][ALM] | 5 sec | Medium
61 | 61 | Circuit Breaker Status | [ELEC][CB][STS] | 5 sec | Medium