## Evap Cooler Points
Point_Description | Point_Name | ALARM DELAY | NOTIFICATION LEVEL
DAHU
Evaporative Cooler 1 Stage 1 Flow Alarm | [EVAP1][STG1][FLOW][ALM] | 5 sec | High
Evaporative Cooler 1 Stage 2 Flow Alarm | [EVAP1][STG2][FLOW][ALM] | 5 sec | High
Evaporative Cooler 2 Stage 1 Flow Alarm | [EVAP2][STG1][FLOW][ALM] | 5 sec | High
Evaporative Cooler 2 Stage 2 Flow Alarm | [EVAP2][STG2][FLOW][ALM] | 5 sec | High
UPS Power Status | [PWR][UPS][STATUS] | 5 sec | High
Mode Alarm | [BMS][MODE][ALM] | 5 sec | High
Supply Air Temp Setpoint Alarm | [BMS][SAT][STPT][ALM] | 5 sec | High
Supply Fan Speed Alarm | [BMS][SF][SPD][ALM] | 5 sec | Medium
Bypass Damper Lower Limit Alarm | [BYPD][LOWER][ALM] | 60 sec | Medium
Bypass Damper Upper Limit Alarm | [BYPD][UPPER][ALM] | 60 sec | High
Evap Cooler Fan Failure Alarm | [ECFAN][FAIL][ALM] | 5 sec | High
Command | [FEC][CMD] | 30 secs | Medium
Evaporative Cooler P High Water Alarm | [EVAP][HIGH][WATER][ALM] | 5 sec | High
Evaporative Cooler P Low Water Alarm | [EVAP][LOW][WATER][ALM] | 5 sec | High
Lower Limit Status | [FEC][LOWER][STS] | 60 sec | Medium
Upper Limit Status | [FEC][UPPER][STS] | 2 minute | Medium
Filter Differential Pressure Alarm | [FILDP][ALM] | 5 sec | Medium
Pre-Filter | [PREFILTER] | 5 sec | Medium
Final Filter | [FINALFILTER] | 5 sec | Medium
Supply Air Damper Lower Limit Alarm | [SAD][LOWER][ALM] | 5 sec | Medium
Supply Air Damper Upper Limit Alarm | [SAD][UPPER][ALM] | 30 sec | Medium
Supply Air Temp High Alarm | [SAT][HIGH][ALM] | 30 sec | Medium
Supply Air Temp Low Alarm | [SAT][LOW][ALM] | 5 sec | Medium
Level Alarm | [SUMP1][HI][LVL][ALM] | 5 sec | High
Low Level Alarm | [SUMP1][LOW][LVL][ALM] | 5 sec | High
Pump Alarm | [SUMP1][PMP][ALM] | 5 sec | High
Level Alarm | [SUMP2][HI][LVL][ALM] | 5 sec | High
Low Level Alarm | [SUMP2][LOW][LVL][ALM] | 5 sec | High
Pump Alarm | [SUMP2][PMP][ALM] | 5 sec | High
UPS Power | [UPS][POWER] | 5 sec | High
UPS Power | [UPS][POWER] | 5 sec | High
Supply Air Temp Temperature Sensor 1 | [SAT][T1] | 5 sec | High
Supply Air Temp Temperature Sensor 2 | [SAT][T2] | 5 sec | High
Supply Air Temp | [SAT] | 30 sec | High
Dedicated AHU Supply Fan Alarm | [DAHU][SF][ALM] | 5 sec | High
Dedicated AHU Filter Differential Pressure Alarm | [DAHU][FILDP][ALM] | 5 sec | Medium
Dedicated AHU Supply Air Temp High Alarm | [DAHU][SAT][HIGH][ALM] | 30 sec | Medium
Air Handling Unit Supply Fan Alarm | [AHU][SF][ALM] | 5 sec | High
Air Handling Unit Filter Differential Pressure Alarm | [AHU][FILDP][ALM] | 5 sec | Medium
Air Handling Unit Supply Air Temp Low Alarm | [AHU][SAT][LOW][ALM] | 5 sec | Medium
INDUSTRIAL WATER SYSTEM
Industrial Water Pump Failure Alarm | [IWS][PUMP][FAIL][ALM] | 5 sec | High
Industrial Water Tank High Level Alarm | [IWS][TANK][HIGH][LVL][ALM] | 5 sec | High
Industrial Water Tank Low Level Alarm | [IWS][TANK][LOW][LVL][ALM] | 5 sec | High
Industrial Water Flow Alarm | [IWS][FLOW][ALM] | 5 sec | Medium
Industrial Water Filter Differential Pressure Alarm | [IWS][FILDP][ALM] | 5 sec | Medium
Industrial Water Supply Pressure Low Alarm | [IWS][SUPPLY][PRESSURE][LOW][ALM] | 5 sec | High
ELECTRICAL ROOM
Main Breaker Trip Alarm | [ELEC][MAIN][BRKR][TRIP][ALM] | 5 sec | High
Panel Overheat Alarm | [ELEC][PNL][OVERHEAT][ALM] | 10 sec | High
UPS Failure Alarm | [ELEC][UPS][FAIL][ALM] | 5 sec | High
Room Temperature High Alarm | [ELEC][ROOM][TEMP][HIGH][ALM] | 30 sec | Medium
Smoke Detection Alarm | [ELEC][SMOKE][ALM] | 5 sec | High
Power Loss Alarm | [ELEC][POWER][LOSS][ALM] | 5 sec | High
Generator Running Status | [ELEC][GEN][RUN][STS] | 5 sec | Medium
Battery Low Alarm | [ELEC][BATTERY][LOW][ALM] | 10 sec | High
Surge Protection Device Alarm | [ELEC][SPD][ALM] | 5 sec | Medium
Circuit Breaker Status | [ELEC][CB][STS] | 5 sec | Medium