## Summary
Equipment | Point_Name | Alarm_Class | CPL_Level | Class_Result | Delay | CPL_Delay | Delay_Result | High_Limit | CPL_High | High_Result | Low_Limit | CPL_Low | Low_Result | Dead_Band | CPL_DB | DB_Result | Trend_Interval | Overall
AHU1 | AHU1_FANSTATUS | High |  | REVIEW |  |  | REVIEW | [10 empty] | NOT IN CPL
AHU1 | AHU1_ESTOP | High |  | REVIEW |  |  | REVIEW | [10 empty] | NOT IN CPL
AHU2 | AHU2_FANSTATUS | High |  | REVIEW |  |  | REVIEW | [10 empty] | NOT IN CPL
AHU2 | AHU2_ESTOP | High |  | REVIEW |  |  | REVIEW | [10 empty] | NOT IN CPL
AHU3 | AHU3_FANSTATUS | High |  | REVIEW |  |  | REVIEW | [10 empty] | NOT IN CPL
AHU3 | AHU3_ESTOP | High |  | REVIEW |  |  | REVIEW | [10 empty] | NOT IN CPL
AHU1 | AHU1_EVAP1_STG1_FLOW_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_EVAP1_STG2_FLOW_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_EVAP2_STG1_FLOW_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_EVAP2_STG2_FLOW_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_PWR_UPS_STATUS | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_BMS_MODE_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_BMS_SAT_STPT_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_BMS_SF_SPD_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_BYPD_LOWER_ALM | Medium | MEDIUM | MATCH | 60 | 60 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_BYPD_UPPER_ALM | Medium | HIGH | MISMATCH | 60 | 60 sec | MATCH | [9 empty] | 1 | NON-COMPLIANT
AHU1 | AHU1_ECFAN_FAIL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_EVAP_HIGH_WATER_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_EVAP_LOW_WATER_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_FILDP_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_SAD_LOWER_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_SAD_UPPER_ALM | Medium | MEDIUM | MATCH | 20 | 30 sec | MISMATCH | [9 empty] | 1 | NON-COMPLIANT
AHU1 | AHU1_SAT_HIGH_ALM | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_SAT_LOW_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_SUMP1_HI_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_SUMP1_LOW_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_SUMP1_PMP_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_SUMP2_HI_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_SUMP2_LOW_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1_SUMP2_PMP_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_EVAP1_STG1_FLOW_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_EVAP1_STG2_FLOW_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_EVAP2_STG1_FLOW_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_EVAP2_STG2_FLOW_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_PWR_UPS_STATUS | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_BMS_MODE_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_BMS_SAT_STPT_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_BMS_SF_SPD_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_BYPD_LOWER_ALM | Medium | MEDIUM | MATCH | 60 | 60 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_BYPD_UPPER_ALM | High | HIGH | MATCH | 60 | 60 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_ECFAN_FAIL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_EVAP_HIGH_WATER_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_EVAP_LOW_WATER_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_FILDP_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_SAD_LOWER_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_SAD_UPPER_ALM | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_SAT_HIGH_ALM | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_SAT_LOW_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_SUMP1_HI_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_SUMP1_LOW_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_SUMP1_PMP_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_SUMP2_HI_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_SUMP2_LOW_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2_SUMP2_PMP_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_EVAP1_STG1_FLOW_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_EVAP1_STG2_FLOW_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_EVAP2_STG1_FLOW_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_EVAP2_STG2_FLOW_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_PWR_UPS_STATUS | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_BMS_MODE_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_BMS_SF_SPD_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_BYPD_LOWER_ALM | Medium | MEDIUM | MATCH | 60 | 60 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_BYPD_UPPER_ALM | High | HIGH | MATCH | 60 | 60 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_ECFAN_FAIL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_EVAP_HIGH_WATER_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_EVAP_LOW_WATER_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_FILDP_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_SAD_LOWER_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_SAD_UPPER_ALM | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_SAT_HIGH_ALM | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_SAT_LOW_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_SUMP1_HI_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_SUMP1_LOW_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_SUMP1_PMP_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_SUMP2_HI_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_SUMP2_LOW_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3_SUMP2_PMP_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS1 | IWS1_PUMP_FAIL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS1 | IWS1_TANK_HIGH_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS1 | IWS1_TANK_LOW_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS1 | IWS1_FLOW_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS1 | IWS1_FILDP_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS1 | IWS1_SUPPLY_PRESSURE_LOW_ALM | Medium | HIGH | MISMATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | NON-COMPLIANT
IWS2 | IWS2_PUMP_FAIL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS2 | IWS2_TANK_HIGH_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS2 | IWS2_TANK_LOW_LVL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS2 | IWS2_FLOW_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS2 | IWS2_FILDP_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS2 | IWS2_SUPPLY_PRESSURE_LOW_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1_MAIN_BRKR_TRIP_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1_PNL_OVERHEAT_ALM | High | HIGH | MATCH | 10 | 10 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1_UPS_FAIL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1_ROOM_TEMP_HIGH_ALM | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1_SMOKE_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1_POWER_LOSS_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1_GEN_RUN_STS | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1_BATTERY_LOW_ALM | High | HIGH | MATCH | 5 | 10 sec | MISMATCH | [9 empty] | 1 | NON-COMPLIANT
ELEC1 | ELEC1_SPD_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1_CB_STS | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2_MAIN_BRKR_TRIP_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2_PNL_OVERHEAT_ALM | High | HIGH | MATCH | 10 | 10 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2_UPS_FAIL_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2_ROOM_TEMP_HIGH_ALM | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2_SMOKE_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2_POWER_LOSS_ALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2_GEN_RUN_STS | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2_BATTERY_LOW_ALM | High | HIGH | MATCH | 10 | 10 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2_SPD_ALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2_CB_STS | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
CAT1 | CAT1_SPACE_TEMP | High | HIGH | MATCH | 5 | 5 sec | MATCH | 78 | 78 | MATCH | 65 | 65 | MATCH | 3 | 2 | MISMATCH | 2 | NON-COMPLIANT
CAT1 | CAT1_SPACE_HUMIDITY | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | 70 | 60 | MISMATCH | 30 | 30 | MATCH | 5 | 5 | MATCH | 2 | NON-COMPLIANT
CAT1 | CAT1_SPACE_CO2 | High | HIGH | MATCH | 10 | 10 sec | MATCH | 1000 | 1000 | MATCH | 400 | 400 | MATCH | 50 | 50 | MATCH | 2 | COMPLIANT
CAT1 | CAT1_SUPPLY_TEMP | High | HIGH | MATCH | 5 | 5 sec | MATCH | 75 | 75 | MATCH | 55 | 55 | MATCH | 2 | 2 | MATCH | 2 | COMPLIANT
CAT1 | CAT1_RETURN_TEMP | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | 80 | 80 | MATCH | 60 | 60 | MATCH | 2 | 2 | MATCH | 2 | COMPLIANT
CAT2 | CAT2_SPACE_TEMP | High | HIGH | MATCH | 5 | 5 sec | MATCH | 78 | 78 | MATCH | 65 | 65 | MATCH | 2 | 2 | MATCH | 2 | COMPLIANT
CAT2 | CAT2_SPACE_HUMIDITY | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | 60 | 60 | MATCH | 30 | 30 | MATCH | 5 | 5 | MATCH | 2 | COMPLIANT
CAT2 | CAT2_SUPPLY_TEMP | High | HIGH | MATCH | 5 | 5 sec | MATCH | 75 | 75 | MATCH | 55 | 55 | MATCH | 2 | 2 | MATCH | 2 | COMPLIANT
CAT2 | CAT2_RETURN_TEMP | Medium | MEDIUM | MATCH | 30 | 5 sec | MISMATCH | 80 | 80 | MATCH | 50 | 60 | MISMATCH | 2 | 2 | MATCH | 2 | NON-COMPLIANT

## Design_Not_Built
CPL_Key | Description | CPL_Level | CPL_Delay
FECCMD | Command | MEDIUM | 30 sec
FECLOWERSTS | Lower Limit Status | MEDIUM | 60 sec
FECUPPERSTS | Upper Limit Status | MEDIUM | 120 sec
FILDPALM | Filter Differential Pressure Alarm | MEDIUM | 5 sec
PREFILTER | Pre-Filter | MEDIUM | 5 sec
FINALFILTER | Final Filter | MEDIUM | 5 sec
SATLOWALM | Supply Air Temp Low Alarm | MEDIUM | 5 sec
UPSPOWER | UPS Power | HIGH | 5 sec
SATT1 | Supply Air Temp Temperature Sensor 1 | HIGH | 5 sec
SATT2 | Supply Air Temp Temperature Sensor 2 | HIGH | 5 sec
SAT | Supply Air Temp | HIGH | 30 sec
DAHUSFALM | Dedicated AHU Supply Fan Alarm | HIGH | 5 sec
DAHUFILDPALM | Dedicated AHU Filter Differential Pressure Alarm | MEDIUM | 5 sec
DAHUSATHIGHALM | Dedicated AHU Supply Air Temp High Alarm | MEDIUM | 30 sec
AHUSFALM | Air Handling Unit Supply Fan Alarm | HIGH | 5 sec

## Stats
Vendor | schneider
Points evaluated | 118
Fully compliant | 105
Non-compliant (rule mismatch) | 7
Not found in CPL (manual review) | 6
Designed but not built | 15
Category | Count
Compliant | 105
Rule mismatch | 7
Manual review | 6
Not built | 15