## Summary
Equipment | Point_Name | Alarm_Class | CPL_Level | Class_Result | Delay | CPL_Delay | Delay_Result | High_Limit | CPL_High | High_Result | Low_Limit | CPL_Low | Low_Result | Dead_Band | CPL_DB | DB_Result | Trend_Interval | Overall
AHU1 | AHU1FANSTATUS | High |  | REVIEW |  |  | REVIEW | [10 empty] | NOT IN CPL
AHU1 | AHU1ESTOP | High |  | REVIEW |  |  | REVIEW | [10 empty] | NOT IN CPL
AHU2 | AHU2FANSTATUS | High |  | REVIEW |  |  | REVIEW | [10 empty] | NOT IN CPL
AHU2 | AHU2ESTOP | High |  | REVIEW |  |  | REVIEW | [10 empty] | NOT IN CPL
AHU3 | AHU3FANSTATUS | High |  | REVIEW |  |  | REVIEW | [10 empty] | NOT IN CPL
AHU3 | AHU3ESTOP | High |  | REVIEW |  |  | REVIEW | [10 empty] | NOT IN CPL
AHU1 | AHU1EVAP1STG1FLOWALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1EVAP1STG2FLOWALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1EVAP2STG1FLOWALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1EVAP2STG2FLOWALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1PWRUPSSTATUS | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1BMSMODEALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1BMSSATSTPTALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1BMSSFSPDALM | High | MEDIUM | MISMATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | NON-COMPLIANT
AHU1 | AHU1BYPDLOWERALM | Medium | MEDIUM | MATCH | 60 | 60 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1BYPDUPPERALM | High | HIGH | MATCH | 60 | 60 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1ECFANFAILALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1EVAPHIGHWATERALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1EVAPLOWWATERALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1FILDPALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1SADLOWERALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1SADUPPERALM | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1SATHIGHALM | Medium | MEDIUM | MATCH | 45 | 30 sec | MISMATCH | [9 empty] | 1 | NON-COMPLIANT
AHU1 | AHU1SATLOWALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1SUMP1HILVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1SUMP1LOWLVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1SUMP1PMPALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1SUMP2HILVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1SUMP2LOWLVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU1 | AHU1SUMP2PMPALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2EVAP1STG1FLOWALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2EVAP1STG2FLOWALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2EVAP2STG1FLOWALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2EVAP2STG2FLOWALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2PWRUPSSTATUS | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2BMSMODEALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2BMSSATSTPTALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2BMSSFSPDALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2BYPDLOWERALM | Medium | MEDIUM | MATCH | 60 | 60 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2BYPDUPPERALM | High | HIGH | MATCH | 60 | 60 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2ECFANFAILALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2EVAPHIGHWATERALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2EVAPLOWWATERALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2FILDPALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2SADLOWERALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2SADUPPERALM | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2SATHIGHALM | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2SATLOWALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2SUMP1HILVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2SUMP1LOWLVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2SUMP1PMPALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2SUMP2HILVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2SUMP2LOWLVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU2 | AHU2SUMP2PMPALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3EVAP1STG1FLOWALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3EVAP1STG2FLOWALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3EVAP2STG1FLOWALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3EVAP2STG2FLOWALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3PWRUPSSTATUS | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3BMSMODEALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3BMSSATSTPTALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3BMSSFSPDALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3BYPDLOWERALM | Medium | MEDIUM | MATCH | 60 | 60 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3BYPDUPPERALM | High | HIGH | MATCH | 60 | 60 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3ECFANFAILALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3EVAPHIGHWATERALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3EVAPLOWWATERALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3SADLOWERALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3SADUPPERALM | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3SATHIGHALM | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3SATLOWALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3SUMP1HILVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3SUMP1LOWLVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3SUMP1PMPALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3SUMP2HILVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3SUMP2LOWLVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
AHU3 | AHU3SUMP2PMPALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS1 | IWS1PUMPFAILALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS1 | IWS1TANKHIGHLVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS1 | IWS1TANKLOWLVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS1 | IWS1FLOWALM | High | MEDIUM | MISMATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | NON-COMPLIANT
IWS1 | IWS1FILDPALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS1 | IWS1SUPPLYPRESSURELOWALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS2 | IWS2PUMPFAILALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS2 | IWS2TANKHIGHLVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS2 | IWS2TANKLOWLVLALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS2 | IWS2FLOWALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS2 | IWS2FILDPALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
IWS2 | IWS2SUPPLYPRESSURELOWALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1MAINBRKRTRIPALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1PNLOVERHEATALM | High | HIGH | MATCH | 10 | 10 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1UPSFAILALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1ROOMTEMPHIGHALM | Medium | MEDIUM | MATCH | 60 | 30 sec | MISMATCH | [9 empty] | 1 | NON-COMPLIANT
ELEC1 | ELEC1SMOKEALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1POWERLOSSALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1GENRUNSTS | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1BATTERYLOWALM | High | HIGH | MATCH | 10 | 10 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1SPDALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC1 | ELEC1CBSTS | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2MAINBRKRTRIPALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2PNLOVERHEATALM | High | HIGH | MATCH | 10 | 10 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2UPSFAILALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2ROOMTEMPHIGHALM | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2SMOKEALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2POWERLOSSALM | High | HIGH | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2GENRUNSTS | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2BATTERYLOWALM | High | HIGH | MATCH | 10 | 10 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2SPDALM | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
ELEC2 | ELEC2CBSTS | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | [9 empty] | 1 | COMPLIANT
CAT1 | CAT1SPACETEMP | High | HIGH | MATCH | 5 | 5 sec | MATCH | 80 | 78 | MISMATCH | 65 | 65 | MATCH | 2 | 2 | MATCH | 2 | NON-COMPLIANT
CAT1 | CAT1SPACEHUMIDITY | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | 60 | 60 | MATCH | 30 | 30 | MATCH | 5 | 5 | MATCH | 2 | COMPLIANT
CAT1 | CAT1SPACECO2 | High | HIGH | MATCH | 10 | 10 sec | MATCH | 1000 | 1000 | MATCH | 300 | 400 | MISMATCH | 50 | 50 | MATCH | 2 | NON-COMPLIANT
CAT1 | CAT1SUPPLYTEMP | High | HIGH | MATCH | 5 | 5 sec | MATCH | 75 | 75 | MATCH | 55 | 55 | MATCH | 2 | 2 | MATCH | 2 | COMPLIANT
CAT1 | CAT1RETURNTEMP | Medium | MEDIUM | MATCH | 5 | 5 sec | MATCH | 80 | 80 | MATCH | 60 | 60 | MATCH | 2 | 2 | MATCH | 2 | COMPLIANT
CAT2 | CAT2SPACETEMP | High | HIGH | MATCH | 5 | 5 sec | MATCH | 78 | 78 | MATCH | 65 | 65 | MATCH | 2 | 2 | MATCH | 2 | COMPLIANT
CAT2 | CAT2SPACEHUMIDITY | Medium | MEDIUM | MATCH | 30 | 30 sec | MATCH | 60 | 60 | MATCH | 30 | 30 | MATCH | 5 | 5 | MATCH | 2 | COMPLIANT
CAT2 | CAT2SPACECO2 | High | HIGH | MATCH | 10 | 10 sec | MATCH | 1000 | 1000 | MATCH | 400 | 400 | MATCH | 50 | 50 | MATCH | 2 | COMPLIANT
CAT2 | CAT2SUPPLYTEMP | High | HIGH | MATCH | 5 | 5 sec | MATCH | 75 | 75 | MATCH | 55 | 55 | MATCH | 5 | 2 | MISMATCH | 2 | NON-COMPLIANT

## Design_Not_Built
CPL_Key | Description | CPL_Level | CPL_Delay
FECCMD | Command | MEDIUM | 30 sec
FECLOWERSTS | Lower Limit Status | MEDIUM | 60 sec
FECUPPERSTS | Upper Limit Status | MEDIUM | 120 sec
FILDPALM | Filter Differential Pressure Alarm | MEDIUM | 5 sec
PREFILTER | Pre-Filter | MEDIUM | 5 sec
FINALFILTER | Final Filter | MEDIUM | 5 sec
SATLOWALM | Supply Air Temp Low Alarm | MEDIUM | 5 sec
UPSPOWER | UPS Power | HIGH | 5 sec
SATT1 | Supply Air Temp Temperature Sensor 1 | HIGH | 5 sec
SATT2 | Supply Air Temp Temperature Sensor 2 | HIGH | 5 sec
SAT | Supply Air Temp | HIGH | 30 sec
DAHUSFALM | Dedicated AHU Supply Fan Alarm | HIGH | 5 sec
DAHUFILDPALM | Dedicated AHU Filter Differential Pressure Alarm | MEDIUM | 5 sec
DAHUSATHIGHALM | Dedicated AHU Supply Air Temp High Alarm | MEDIUM | 30 sec
AHUSFALM | Air Handling Unit Supply Fan Alarm | HIGH | 5 sec

## Stats
Vendor | siemens
Points evaluated | 118
Fully compliant | 105
Non-compliant (rule mismatch) | 7
Not found in CPL (manual review) | 6
Designed but not built | 15
Category | Count
Compliant | 105
Rule mismatch | 7
Manual review | 6
Not built | 15